## Sheet1
ANALOG TO SPEED REFERENCE CALCULATOR
PF520 Series Analog Input at Target Speed in Hz
Drive Configuration |  |  |  |  | Required input fields
Min Freq. (P043) | 10 | Hz
Max Freq. (P044) | 50 | Hz |  |  | Notes:
Frequency Span | 40 | Hz
Minimum Analog Signal (mA) | 4 | Anlg 4-20 or 0-10V |  |  | If Min and Max Frequencies are changed
Maximum Analog Signal (mA) | 20 | Anlg 4-20 or 0-10V |  |  | Anlg Lo and Anlg Hi will be adjusted by calculator
Analog Span | 16 | Anlg 4-20 or 0-10V
Anlg Lo (T95) Drive setting | 16.67% | Percentage to set T95
Anlg Hi (T96) Drive setting | 83.33% | Percentage to set T96
Analog Offset | 4 | Offset for 4-20mA "0" if 0-10VDC
Ratio of analog units/hz of drive | 0.4 | mA/Hz or V/Hz
Desired test speed in hz | 45 | Hz
Analog value needed to run at test speed |  |  | 18 | mA or V | ESTIMATED TARGET ANALOG VALUE FOR DRIVE